## EQUIPMENT SUMMARY
Campus - Building Name
[type of building]
[schedule]
Equip Category | Equip | Details | BAS Graphic | BAS Setpoints | Mech Drawing | Sequence of Operation
ON GRAFANA:
Airside Equipment | AHU-1 | serves classrooms and offices | AHU1.JPG [Link graphics that refer to the equipment]
Boiler Plant | HW Plant |  | Reheat HX 1 & 2.JPG
Chiller Plant | PCHWP1 |  | Chilled Water System.JPG
NOT YET ON GRAFANA:
Chiller Plant | PCHWP2 |  | Chilled Water System.JPG
Source(s): Farmingdale SOB Equip List BAS Screen Shots [Include Equipment Inventory Link and BAS Screenshot Folders Link]

## RECOMMENDATIONS
Campus - Building Name
Equip | Trend Chart | Finding(s) | Next Step(s) | Owner | Priority | Status | Updates | Estimated Costs | Actual Costs | Estimated Labor Hours | Actual Labor Hours
SESSION X - Date
Equipment | BOCS Trend Chart (Dates) | Findings notes while reviewing the trend charts | Next Steps instructions | N/A | N/A | N/A | Updates on the Next Steps
AHU-3 | 01 Fan Schedule (10/10 - 10/15) | Fans are running 24/7 | Change unit schedule to follow occupancy schedule | Contractor | High | Not Started | on the list of controls contractor
AHU-1 | 07 RA/Space Temp Control (10/10 - 10/15) | Economizing well in mild weather; econ enabled when OAT < 70°F, may be better at 65°F in more humid months | Monitor to make sure economizer enabled above 65°F in more humid months does not become an issue | BuildingCoach Campus Team | Medium | Deferred | for spring/summer months
SESSION Y - Date
HW Plant (HX from district steam) | 26 (10/25 - 11/1) | HWST-SP is 185F no HWST reset delta-T is 10-15F DP-SP stays at 4 inwc | Investigate if it is possible to add a HW reset to this loop; | BuildingCoach Campus Team | Low | Completed